## Slide 1
What is a
Digital Twin?
VoltMind
A software copy of a transformer that follows its live measurements and checks them against what physics says should be happening.
Transformer
The physical asset
SCADA
Time-stamped sensor data
Virtual model
Expected thermal behaviour
Assessment
Evidence and uncertainty
Maintenance
Engineer makes the call
Twin, not dashboard: it stays in step with the data, predicts what the asset should do, and feeds a decision.
Built today: replay of recorded SCADA data. Live sensor feeds are the next stage.
Team [Team Name] · Problem Statement [ID] · [College] · Mentor [Name]
Notes: A transformer is the physical equipment that supplies electricity. Its digital twin is a software copy that is kept up to date with measurements from the real unit. VoltMind compares what actually happened with what the physics says should have happened, then shows the evidence so an engineer can investigate.
If a judge asks why this is a twin and not a dashboard: a dashboard only shows values. The twin keeps a model in step with the asset, predicts the expected response, and turns the gap into evidence for a decision.
Be clear about scope: today the twin runs on recorded (synthetic) SCADA data replayed in time order. It is decision support. It does not switch or control anything.
SCADA = Supervisory Control and Data Acquisition. Fill in the team line at the bottom before presenting.
Transition: why is a temperature reading on its own not enough?

## Slide 2
The Problem: One Reading, Many Meanings
Fixed temperature alarms cannot tell a normal hot afternoon from a developing fault.
VOLTMIND / DISTRIBUTION TRANSFORMER DIGITAL TWIN / DIGITAL TWIN HACKATHON · ORGANISED BY CPRI
02 / 10
75 °C
Normal under heavy load? Worrying at light load? Or just a bad sensor?
LOAD
How much current is the transformer carrying?
AMBIENT
How hot is the air around it?
HISTORY
Has the oil had time to heat up or cool down?
TRUST
Are the sensor, timing and calibration credible?
≈1.3 million
distribution transformers reported failing in India each year (Mercom India, Nov 2025)
2× faster
insulation ageing for every sustained 6 °C of extra hot-spot temperature (IEC 60076-7)
75 °C is an example, not a threshold. Protection limits stay; VoltMind adds context.
Notes: Take the 75 °C example and ask what produced it. Heavy load and a hot afternoon could make it normal. The same number on a light-load winter night could be a problem. Oil temperature also reacts slowly, so the recent past matters, and a faulty sensor can imitate an overheating transformer.
Why small gaps matter: IEC 60076-7 describes insulation ageing roughly doubling for every 6 °C of sustained extra hot-spot temperature. We measure top-oil, not hot-spot, so use this as motivation only.
The 1.3 million figure comes from a Mercom India report (28 Nov 2025) on Central Electricity Authority measures. Check the wording against the source before presenting.
Context does not replace protection equipment and does not prove which component failed.
Transition: show how the whole system turns data into evidence.

## Slide 3
System Architecture: Measurements to Decisions
Three running services and one traceable path from raw data to an engineer's decision.
VOLTMIND / DISTRIBUTION TRANSFORMER DIGITAL TWIN / DIGITAL TWIN HACKATHON · ORGANISED BY CPRI
03 / 10
SCADA SOURCE
Local replay or uploaded file
CSV, TSV, TXT, XLSX, JSON. Live gateway planned.
SPRING BOOT · :8080
Session control and API proxy
Everything runs locally today
PYTHON ML · :8765
Normalise, validate, infer
Thermal physics + rating-specific models
TWIN INTELLIGENCE
Five investigation modules
100 kVA transformer
INPUT CONTRACT
Schema, units and time order must be valid before anything is replayed
REACT + VITE · :5173
Trends, alarms, evidence and a local assistant
LOCAL ASSISTANT
Answers from a fresh summary of the backend. It is not an external chatbot.
SQLITE
Incident history and the maintenance records engineers enter
REST requests
SSE replay stream
Why this split: Python owns the data science, Spring Boot owns sessions and the API, React stays a thin evidence view. A live SCADA feed can replace the replay source without touching the rest.
Notes: Follow one file through the system. It enters through the backend. Spring Boot manages the session and proxies a persistent Python service. Python normalises the measurements, runs the thermal physics and the model, and produces the intelligence. React asks for evidence over REST and receives the replay as server-sent events.
SQLite keeps de-duplicated incidents and any maintenance records the engineer types in. Ports: frontend 5173, backend 8080, ML service 8765.
The diagram shows who owns what. It is not an independent live IoT gateway. Live utility ingestion is future work. The assistant is a deterministic local evidence interface, not a general-purpose LLM.
Transition: zoom into the intelligence inside the Python service.

## Slide 4
Inside VoltMind: Physics First, Then ML
The model flags departures from expected behaviour. Engineers interpret the evidence.
VOLTMIND / DISTRIBUTION TRANSFORMER DIGITAL TWIN / DIGITAL TWIN HACKATHON · ORGANISED BY CPRI
04 / 10
1 MEASURE
3-phase voltage and current, ambient, top-oil
2 EXPECT
First-order top-oil model, calibrated per asset
3 RESIDUAL
Actual minus expected, past readings only
4 CLASSIFY
Logistic Regression on those 4 features
5 ASSESS
Health Index, confidence, or "not assessed"
Chart: Top-oil (°C)
ONE DAY OF SYNTHETIC REPLAY · 100 kVA · 1 Jan 2026
Peak gap 10.0 °C at 21:45
Above 2 °C from 12:35 onward
THE FOUR RESIDUAL FEATURES
Residual now
Mean of last 30 min and last 60 min
Change over the last 30 min
Only past readings are used (causal).
RUNS IN PARALLEL
Electrical and data-quality checks: missing sensors, outage, overload, undervoltage, imbalance
Health Index updates every 24 readings (2 h). Alarms stay immediate. It is an observation index, not a failure probability.
Notes: Read the top row left to right. Measurements drive a calibrated first-order thermal model that says what top-oil temperature to expect. Actual minus expected is the residual, turned into four features for the 100 kVA Logistic Regression classifier. In parallel, electrical and data-quality checks run on the same data. Their results are kept separate from the classifier so each one can be questioned on its own.
The chart is one synthetic day (288 five-minute readings, no interpolation). From about 12:35 the measured oil runs above the physics expectation and the gap peaks at 10.0 °C at 21:45. Say what it is: a persistent gap that deserves investigation, not a named failure.
Technical detail: next state = alpha x previous state + (1 - alpha) x previous equilibrium, alpha = exp(-5/tau). The Health Index publishes every 24 processed readings. Where data are insufficient the system abstains instead of guessing.
The thermal model uses the same exponential top-oil form as loading guides such as IEC 60076-7 and IEEE C57.91 (loss-ratio load term, exponent 0.8); it is calibrated per asset and is not a certified implementation of either standard. Confirm this wording with the team before presenting.
The Health Index is an engineering observation index. It is not a failure probability, insulation health or remaining useful life.
Transition: what data did we build and test this on?

## Slide 5
Our SCADA Datasets
580,608 rows across three ratings. All synthetic. None are field measurements.
VOLTMIND / DISTRIBUTION TRANSFORMER DIGITAL TWIN / DIGITAL TWIN HACKATHON · ORGANISED BY CPRI
05 / 10
100 kVA
FLAGSHIP
241,920
rows · 60 replays × 14 days
5-minute readings, 288 per day
250 kVA
145,152
rows · 24 replays × 21 days
5-minute readings, 288 per day
630 kVA
193,536
rows · 24 replays × 28 days
5-minute readings, 288 per day
EACH ROW HOLDS
Timestamp and communication status
Three-phase voltage and current
Ambient and top-oil temperature
Optional oil level and R-terminal temperature
SCENARIO DESIGN
Healthy running mixed with labelled events: thermal, electrical, sensor, communication, data quality, oil level and terminal.
WHY SYNTHETIC
Every injected event has a known start and type, so detection can be scored honestly. Real SCADA rarely comes with that ground truth.
FIELDS ARE NOT INPUTS
Scenario and offline channels sit in the files but never feed the classifier.
It sees only four residual features.
Notes: Row counts are plain arithmetic: replays x days x 288 five-minute readings per day. 100 kVA: 60 x 14 x 288 = 241,920. 250 kVA: 24 x 21 x 288 = 145,152. 630 kVA: 24 x 28 x 288 = 193,536. Total 580,608.
Say clearly that these are synthetic SCADA populations, not field measurements. If asked why synthetic: we know the exact start and type of every injected event, which lets us score detection honestly. Real SCADA rarely comes with that ground truth.
The fresh test set (48,384 rows) was generated and held out after the 100 kVA model was locked.
A dataset can hold more columns than a model uses. Scenario labels and offline channels are in the files, but the 100 kVA classifier only receives four residual features computed from past measurements.
Transition: now the three detectors built on these data.

## Slide 6
Three Transformers, Three Rating-Specific Detectors
Each rating has its own locked runtime. Two use trained ML; 630 kVA is physics-based.
VOLTMIND / DISTRIBUTION TRANSFORMER DIGITAL TWIN / DIGITAL TWIN HACKATHON · ORGANISED BY CPRI
06 / 10
100 kVA · FLAGSHIP
250 kVA
630 kVA
Detector
Logistic Regression
4 thermal features
Histogram Gradient Boosting
13 features
Physics-based causal detector
No trained classifier
Delivered data
241,920 rows
60 replays × 14 days
145,152 rows
24 replays × 21 days
193,536 rows
24 replays × 28 days
Rating treatment
Asset-bound calibration
and guarded inference
Frozen nominal features
plus electrical screens
Rating-specific dynamics
and time-constant warm-up
Advanced modules
All five investigation
modules built
Shared monitoring UI
Extension planned
Shared monitoring UI
Extension planned
WHY THEY DIFFER
Ratings have different thermal time constants and rated currents (100 kVA at 433 V is about 133 A per phase), so one shared model would be wrong.
KEPT SEPARATE
Oil-level and terminal-temperature analysis are optional add-ons, not part of the core thermal classifier. No cross-rating accuracy ranking is claimed.
Notes: Be precise here: we did not train three ML classifiers. We built three rating-specific detection systems. The 100 kVA detector is a Logistic Regression thermal classifier. The 250 kVA detector is a Histogram Gradient Boosting classifier. The 630 kVA detector is a physics-based causal detector, and we label it that way because that is what it is.
Each rating has its own thermal constants, current references and readiness rules, so they are not interchangeable. 100 kVA at 433 V line-to-line gives about 133.3 A rated phase current.
The datasets are different benchmarks, so we do not rank accuracy across ratings. The experimental oil-level and R-terminal heads are separate from the core thermal classifier. We do not claim validated bushing-fault, short-circuit or remaining-life diagnosis.
Transition: show the working 100 kVA application.

## Slide 7
VoltMind in Action: A Working Application
Screenshot from the running prototype: 4,032-reading replay on 100 kVA synthetic data.
VOLTMIND / DISTRIBUTION TRANSFORMER DIGITAL TWIN / DIGITAL TWIN HACKATHON · ORGANISED BY CPRI
07 / 10
1
2
3
4
1
WORKSPACES
Overview, Live Twin, Analytics, Alerts, Maintenance, Assets, Intelligence Lab, Fault Investigation.
2
ACTUAL VS EXPECTED
Measured top-oil beside the thermal expectation and their deviation.
3
THE TWIN COMPARISON
A widening gap matters more than a single temperature.
4
EVIDENCE ASSISTANT
Answers from the local data: 4,032 of 4,032 readings replayed, 631 thermal-alert readings, 3,830 assessable.
Alerts are evidence to investigate, not confirmed failures.
SELECT
PROCESS
COMPARE
DETECT
EXPLAIN
Notes: This is a capture from the running application, not a mock-up. Walk the numbered points: the workspaces across the top, the actual and expected top-oil tiles, the central comparison chart, and the VoltMind Insights panel.
The panel says 4,032 of 4,032 readings processed and 3,830 of 4,032 thermal readings assessable. The remaining readings are explicitly left unassessed. Gaps in the source data are shown as gaps and are never filled in with invented values.
During the live demo: pick a rating, load local or uploaded data, play the replay, pause on a gap between measured and expected oil, open an incident, then ask the assistant 'What faults were detected?' and download the evidence.
The assistant answers supported questions from a local backend summary. It is not a general-purpose LLM.
Keep the live application open in a second window in case the judges want to see another tab.

## Slide 8
Why VoltMind Is Different
Most dashboards stop at the alert. These five tools help an engineer decide what to do next.
VOLTMIND / DISTRIBUTION TRANSFORMER DIGITAL TWIN / DIGITAL TWIN HACKATHON · ORGANISED BY CPRI
08 / 10
1
What-If Simulator
“What happens if we reduce load?”
Compares the baseline thermal response with a reduced-load one at constant ambient.
LIMIT Not a failure forecast. Controls nothing.
2
Sensor Investigator
“Is it the transformer or the sensor?”
Keeps sensor explanations and physical explanations side by side.
LIMIT Slow sensor bias can look like real heating.
3
Fault Evidence Report
“Why was this alert raised?”
Records onset, readings, scores, data quality and calibration in a downloadable report.
LIMIT Evidence for review, not a confirmed fault.
4
Falsification Twin
“Did the repair actually work?”
Tracks recurrence and compares matched before/after windows around logged maintenance.
LIMIT Shows association, not proof of cause.
5
Thermal DNA
“Is its heating and cooling response changing?”
Compares clean load-step responses against a verified healthy reference.
LIMIT Can stay "not ready". No damage baseline claimed.
All five read the same twin: the same measurements, calibration and evidence trail. Built and running for 100 kVA; extension to 250 and 630 kVA is planned.
Notes: This is the centrepiece. A normal dashboard tells you something is hot. These five tools help the engineer ask the next question, and each one says what it cannot do.
What-If: simulates a constant-ambient load reduction and compares it with the baseline. It does not predict failure or control equipment.
Sensor Investigator: keeps competing explanations alive instead of picking one. Slow sensor bias may still look like real heating.
Fault Evidence Report: preserves onset, readings, scores, quality and calibration provenance so an alert can be reviewed later.
Falsification Twin: uses recurrence plus logged maintenance. Matching rules: 24-hour windows, load within ten percentage points, ambient within 2 °C, at least 24 matched post-maintenance readings. A repair association is not causal proof.
Thermal DNA: needs at least three clean reference response episodes and three later comparable ones. When the load never excites the transformer enough, it says not ready rather than inventing a reference.
These extend investigation around the frozen classifier. They did not retrain it. Show each on the live app if time allows.
Transition: how do we know the core detector is reliable?

## Slide 9
Validation: How Reliable Is VoltMind?
100 kVA flagship, fresh held-out synthetic benchmark (48,384 rows), tested after the model was locked.
VOLTMIND / DISTRIBUTION TRANSFORMER DIGITAL TWIN / DIGITAL TWIN HACKATHON · ORGANISED BY CPRI
09 / 10
22 / 23
thermal events detected
Median delay 82.5 min, 90th percentile 218 min
93.1%
thermal assessment coverage
Rows the model cannot judge are marked unassessed
0.127
false episodes per healthy day
18 false episodes over 141.8 healthy days: about one every 8 days
BASELINE VS VOLTMIND (SYNTHETIC)
Baseline
VoltMind
Events detected
20 / 23
22 / 23
Coverage
74.8%
93.1%
False episodes / day
0.071
0.127
More detection costs more false alerts. We report that trade-off.
SOFTWARE CHECKS
80 Python tests passed
18 frontend tests passed
209 model and data files preserved byte for byte
Software tests, not field accuracy.
LIMITS WE STATE
Synthetic only. Not yet tested on organiser or field data.
Oil head: 55.2% recall, counting abstentions.
No validated bushing fault, short-circuit or remaining-life diagnosis.
Notes: Lead with the fresh held-out synthetic test on the 100 kVA flagship: 22 of 23 thermal events detected, 93.1% assessment coverage, and 18 false episodes over 141.8 negative-truth days, which is 0.127 per negative day. A false episode is one continuous run of false alerts. In plain words, on healthy days we expect roughly one false episode every eight days. Label every one of these as a synthetic benchmark result.
The 250 and 630 kVA detectors keep their own locked benchmarks. We do not compare accuracy across ratings.
Be upfront about the trade-off. The original thermal baseline detected 20 of 23 events with 74.8% coverage and 0.0705 false episodes per negative day. VoltMind raises detection and coverage but also the false-alarm burden. Median onset delay is 82.5 minutes and the 90th percentile is 218 minutes.
Kill-First means we attacked our own baseline first, inspected the failures, made only justified improvements, revalidated on fresh data, then locked the artifacts.
The 80 Python and 18 frontend tests are software tests, not evidence of field accuracy. The 209 preserved files cover all ratings and show the locked models were not changed afterwards. The oil head catches 55.2% of oil events when abstentions count, and the terminal head is separate again. We do not claim validated bushing-fault, short-circuit or remaining-useful-life diagnosis, and we have not yet tested on organiser or field data.
Transition: what comes next.

## Slide 10
From Prototype to Real-World Impact
The next step is real data. Everything beyond that depends on it.
VOLTMIND / DISTRIBUTION TRANSFORMER DIGITAL TWIN / DIGITAL TWIN HACKATHON · ORGANISED BY CPRI
10 / 10
TODAY
Working prototype
Replay of recorded SCADA data
Three rating-specific detectors
Five investigation tools on 100 kVA
NEXT
Prove it on real assets
Live SCADA / IoT feed
Independent commissioning
Field validation against observations
THEN
Broaden
Investigation tools for 250 and 630 kVA
Better fault diagnosis
Maintenance work-order integration
LATER
Plan ahead
Ageing and remaining-life studies
Fleet-level view across many transformers
Needs long-term field data
FOR MAINTENANCE TEAMS
Look into a developing gap earlier, instead of waiting for a fixed alarm limit.
FOR ASSET REVIEWERS
Every alert carries its readings, scores and data quality, so it can be reviewed.
FOR ENGINEERS
Test whether a repair held, and keep the final call.
Our ask: real transformer SCADA data, so we can test the locked models on real assets.
Impact statements are goals. Savings and failure prevention have not been field-validated.
Notes: Close with what is finished and the next engineering gate: connect independently measured real-asset data, commission the physical transformer, then test the locked models against independent field observations. Only then can operational value be measured.
The ask on the banner is a suggestion. Edit it to match what you actually want from the organisers.
The longer-term aim is a traceable view across many transformers with the engineer in charge. Advanced investigation tools currently exist for 100 kVA only.
We do not claim deployed IoT hardware, physical control, quantified savings, guaranteed failure prediction or validated remaining useful life.
Invite the judges to try the live replay and to ask about input formats, evidence limits or the thermal model.