## Slide 1
VoltMind
Distribution
Transformer Twin
A software model that compares measured transformer temperature with expected behaviour under its electrical load and surrounding air.
Transformer
The physical asset
SCADA
Time-stamped sensor data
Virtual model
Expected thermal behaviour
Assessment
Evidence and uncertainty
Maintenance
Engineer makes the call
The thermal twin adds operating context to measurements and supports an engineer’s investigation.
Local synthetic replay and upload today. Live sensors are future work.
100 kVA flagship with independent 250 and 630 kVA monitoring
Notes: VoltMind is a transformer-specific operational thermal twin prototype. The current interface replays synthetic measurements or accepts uploaded measurements. No physical sensor feed is connected. Expected oil depends causally on preceding electrical loading and ambient. Engineers retain decisions. Source: project README.md; docs/FINAL_IMPLEMENTATION_ARCHITECTURE.md.

## Slide 2
Why temperature needs operating context
The same oil temperature can have different meanings at different loads and ambient conditions.
VOLTMIND DISTRIBUTION TRANSFORMER DIGITAL TWIN SYNTHETIC RESEARCH PROTOTYPE
02 / 10
75 °C
Normal under heavy load? Worrying at light load? Or just a bad sensor?
LOAD
How much current is the transformer carrying?
AMBIENT
How hot is the air around it?
HISTORY
Has the oil had time to heat up or cool down?
TRUST
Are the sensor, timing and calibration credible?
133.34 A
Rated phase current for 100 kVA at 433 V line-to-line. Loading needs the correct rating base.
24 readings
A two-hour assessment at five-minute cadence. Live detector alerts continue between summaries.
75 °C is an example, not a threshold. Protection limits stay; VoltMind adds context.
Notes: 75 °C is an illustrative temperature, not a trained threshold or protection limit. Current base: I_rated=100000/(sqrt(3)*433)=133.34 A. 24 five-minute sample slots form the two-hour publication block. Fixed limits remain useful for protection; the project adds operating context. Removed unsourced national failure numbers and the oversimplified insulation-aging multiplier. Source: ml/integration100.py; ml/assessment_window.py.

## Slide 3
Local architecture and ownership
Python owns replay sessions and inference. Spring Boot proxies APIs. React presents processed evidence.
VOLTMIND DISTRIBUTION TRANSFORMER DIGITAL TWIN SYNTHETIC RESEARCH PROTOTYPE
03 / 10
SCADA SOURCE
Local replay or uploaded file
CSV, TSV, TXT, XLSX, JSON. Live gateway planned.
SPRING BOOT :8080
Allowlisted API proxy
Forwards requests and the replay stream
PYTHON WORKER :8765
Session and replay state
Validation, inference and two-hour summaries
TWIN INTELLIGENCE
Five investigation modules
100 kVA transformer
INPUT CONTRACT
Schema, units and time order must be valid before anything is replayed
REACT + VITE · :5173
Trends, alarms, evidence and a local assistant
LOCAL ASSISTANT
Deterministic explanations from current processed evidence. No external AI service.
SQLITE
Incident history and the maintenance records engineers enter
REST requests
SSE replay stream
Sensor integration needs a gateway adapter, timestamp/unit validation and field calibration. The separated input boundary supports that future work. No live gateway is connected today.
Notes: Worker Manager and Session classes own replay state. Spring Boot is an allowlisted proxy and forwards HTTP/SSE. React shows processed evidence and deterministic local explanations. SQLite stores 100-kVA incidents, maintenance and references. Uploads support explicit mappings and calibrated five-minute inference. A live gateway would require engineering and verification. Sources: ml/service.py; backend/src/main/java/com/example/dtbackend/TransformerController.java; frontend/src/services/monitoringInsights.js; docs/FINAL_INTELLIGENCE.md.

## Slide 4
Thermal inference uses expected behaviour
The 100-kVA thermal head compares actual oil with a commissioned first-order thermal expectation.
VOLTMIND DISTRIBUTION TRANSFORMER DIGITAL TWIN SYNTHETIC RESEARCH PROTOTYPE
04 / 10
1 MEASURE
3-phase voltage and current, ambient, top-oil
2 EXPECT
First-order top-oil model, calibrated per asset
3 RESIDUAL
Actual minus expected, past readings only
4 CLASSIFY
Thermal Logistic Regression
Four residual features
5 ASSESS
Health Index, confidence, or "not assessed"
100-kVA DEMO 10 FEB 2026 FIVE-MINUTE READINGS
All 288 native readings on 10 February. Actual oil stays about 11 °C above expected.
THE FOUR RESIDUAL FEATURES
Residual now
Mean of last 30 min and last 60 min
Change over the last 30 min
Only past readings are used (causal).
PARALLEL CHECKS
Separate oil and R-terminal LR heads. Electrical rules check phase loading, undervoltage and imbalance.
Health/risk publish every 24 rows. Warm-up and missing evidence stay explicit.
Chart: Top-oil (°C)
Notes: Native chart uses all 288 original 10 February 2026 five-minute observations from data/demo100/100kVA_THERMAL_TWIN_DEMO_4032.csv and expected oil computed by unchanged FinalRuntime100 using data/demo100/calibration.json. Maximum residual 11.03498 °C. Chart values rounded to six decimals for Excel portability. No smoothing or fabricated chart data. Thermal LR inputs: current residual, mean 30 min, mean 60 min, change 30 min. Scores are uncalibrated detector scores. Independent asset calibration and causal history are mandatory. Electrical warnings are engineering rules. Sources: ml/integration100.py; ml/final100/ORIGINAL_TRAINING_README.md; data/demo100/validation.json.

## Slide 5
Synthetic data and independent replays
580,608 original monitoring rows plus 4,032 demo rows = 584,640 available replay rows.
VOLTMIND DISTRIBUTION TRANSFORMER DIGITAL TWIN SYNTHETIC RESEARCH PROTOTYPE
05 / 10
100 kVA
FLAGSHIP
245,952
60 original replays + 1 demo
4,032 rows each, 14 days
250 kVA
145,152
rows · 24 replays × 21 days
5-minute readings, 288 per day
630 kVA
193,536
rows · 24 replays × 28 days
5-minute readings, 288 per day
MEASURED CHANNELS
Phase voltages and currents
Ambient and top-oil temperature
Time and availability
Optional oil level / R-terminal sensors vary by dataset
SEPARATE STORIES
Replay IDs identify independent synthetic histories. They do not form one physical asset’s timeline. Training and test files are separate from this replay total.
DEMO PROVENANCE
1–8 Feb: normal response
9–11 Feb: injected heating
12–14 Feb: recovery
Matched model physics makes this an illustration, not an accuracy benchmark.
NO LABEL LEAKAGE
Runtime excludes scenario, truth and latent generator fields.
The 100-kVA heads use 4 thermal, 8 oil and 5 terminal derived features.
Notes: Replay inventory: 100 kVA 241920 original rows plus 4032 demo; 250 kVA 145152; 630 kVA 193536. Total584640. These totals exclude extra training, validation and commissioning copies. Each 4032-row story has 4032 five-minute sample slots, fourteen days, first-to-last time span13d23h55m. Demo is idealized matched-physics illustration and cannot substantiate model generalization. Labels/events/profiles are not runtime features. Source: data/final100; data/demo100; ml/service.py; ml/integration100.py.

## Slide 6
Separate runtimes for each rating
100 kVA is the flagship. Rating-specific calibration and runtime contracts remain separate.
VOLTMIND DISTRIBUTION TRANSFORMER DIGITAL TWIN SYNTHETIC RESEARCH PROTOTYPE
06 / 10
100 kVA · FLAGSHIP
250 kVA
630 kVA
Detector
Three Logistic Regression heads
Thermal 4 / oil 8 / terminal 5 features
Histogram Gradient Boosting
13 features
Physics-based causal detector
No trained classifier
Delivered data
241,920 original rows
+ 4,032 separate demo rows
145,152 rows
24 replays × 21 days
193,536 rows
24 replays × 28 days
Rating treatment
Asset-bound calibration
and guarded inference
Frozen nominal features
plus electrical screens
Rating-specific dynamics
and time-constant warm-up
Advanced modules
All five investigation
modules built
Shared monitoring UI
Extension planned
Shared monitoring UI
Extension planned
RATING MATTERS
Rated phase current and thermal response depend on the transformer. The project uses separate frozen runtimes. A shared model would need explicit cross-rating validation.
DETECTION SCOPE
100-kVA oil depletion and R-terminal heating use separate LR heads. Neither diagnoses internal bushing faults. No cross-rating accuracy ranking is justified.
Notes: One locked 100-kVA V4 bundle holds three independently fitted LR heads: thermal4, oil8, R-terminal5 derived features. Oil features use measured level and oil temperature with configured geometry. Terminal features use R-terminal surface temperature, ambient and current. Optional detectors abstain without evidence. 250 kVA uses its frozen HGB runtime; 630 kVA has a physics detector, no trained classifier. No cross-rating benchmark comparability. Sources: ml/final100/ORIGINAL_TRAINING_README.md; ml/vendor250/MODEL_CARD.md; ml/integration630.py.

## Slide 7
The judge demonstration
A separate 4,032-reading synthetic replay shows normal response, injected excess heat and recovery.
VOLTMIND DISTRIBUTION TRANSFORMER DIGITAL TWIN SYNTHETIC RESEARCH PROTOTYPE
07 / 10
1
NORMAL RESPONSE
1–8 February: actual oil follows expected oil under alternating 35% and 70% loading.
2
EXCESS HEATING
9–11 February: added heat separates actual from expected. The locked detector raises a thermal alert.
3
RECOVERY
12–14 February: the extra heat stops. Oil cools gradually and the detector returns to no alert.
4
COMPLETE REPLAY
4,032 readings processed. One thermal episode recorded. Zero active warnings after recovery.
History retains the warning after recovery.
100 kVA
JUDGE DEMO
60x REPLAY
LIVE TWIN
SELECT DATE
Notes: Demo source is DEMO100_THERMAL_TWIN. At60x4032rows take approximately67seconds plus processing overhead. Select1Feb,10Feb,14Feb in Live Twin. The full replay produced911 thermal-alert rows representing one contiguous episode, not911 independent errors, and eleven thermal warm-up/unassessed rows. First thermal alert9Feb00:55IST. Finalday has zero thermal alerts. Complete browser replay: one recorded thermal episode, zero active warnings, one readiness event. Separate first8days have31clean load-response episodes; this does not automatically lock a DNA reference. UI screenshot is the verified actual app, historical10Feb graph. Sources: data/demo100/validation.json; README.md; docs/PUBLIC_RELEASE_VALIDATION.md; reports/frontend_polish_20261011/thermal-demo-graph.png.

## Slide 8
Investigation tools and evidence limits
Five implemented tools on 100 kVA support review. Each has a clear evidence boundary.
VOLTMIND DISTRIBUTION TRANSFORMER DIGITAL TWIN SYNTHETIC RESEARCH PROTOTYPE
08 / 10
Tool | Implemented contribution | Evidence boundary
What-if simulator | Independent thermal projection after a hypothetical load reduction. | Constant ambient assumptions. No protection action or failure forecast.
Sensor investigator | Presents abrupt jumps, stuck sensors and competing heating explanations. | One oil probe cannot reliably separate slow sensor bias from excess heating.
Fault evidence report | Exports processed readings, onset, scores, quality and calibration context. | A detector warning supports investigation. It does not confirm a failed component.
Falsification Twin | Tracks recurrence and compares load/ambient-matched windows around maintenance. | Matched observations show association. They do not prove repair caused recovery.
Thermal DNA | Compares clean load-step responses with an explicitly verified healthy reference. | Needs sufficient comparable episodes. No inferred damage or fitted lifetime.
Thermal DNA requires at least three clean reference episodes and three comparable new episodes. No automatic healthy baseline.
Notes: Thermal DNA is descriptive screening, not a trained damage detector or genetic information. It extracts steps >=15load percentage points with clean five-minute history, stable load and ambient. Reference requires explicit healthy attestation, provenance, at least3clean episodes and no thermalalert in the reference history. Comparison requires3new comparable episodes after the reference period. Drift screens are engineering assumptions. Falsification Twin matches load/ambient windows around engineer-entered maintenance and reports association. Source: ml/intelligence.py; docs/FINAL_INTELLIGENCE.md.

## Slide 9
Fresh synthetic validation and its trade-offs
Thermal test: 48,384 rows generated after lock. Same simulator family. No field generalization claim.
VOLTMIND DISTRIBUTION TRANSFORMER DIGITAL TWIN SYNTHETIC RESEARCH PROTOTYPE
09 / 10
22 / 23
thermal events detected
Median delay 82.5 min, 90th percentile 218 min
93.1%
thermal assessment coverage
Rows the model cannot judge are marked unassessed
0.127
false episodes per negative-truth day
18 episodes / 141.8 day-equivalents pooled across synthetic histories
BASELINE VS VOLTMIND (SYNTHETIC)
Baseline
VoltMind
Events detected
20 / 23
22 / 23
Coverage
74.8%
93.1%
False episodes / day
0.071
0.127
V4 detects more events sooner, with higher false alarms and lower row precision.
SOFTWARE VERIFICATION
80 Python tests
21 frontend tests
5 Spring Boot tests
209 protected artifacts match exactly
These checks establish software behaviour, not field accuracy.
MODEL LIMITS
One of 23 thermal events missed.
Oil recall including abstentions: 55.2%. Coverage: 55.1%.
No trained pressure, internal bushing, short-circuit or RUL diagnosis.
Notes: Fresh post-lock primary test contains48384rows; optional oil controls add20736rows for69120total oil/terminal evaluation rows. All come from the same simulator family. Thermal22/23events detected, median82.5min,p90218min,coverage93.1238%,18falseepisodes/141.81597negative-truth day-equivalents=.126925. The denominator pools histories and is not a field reliability forecast. Thermal row precision91.33% versus baseline96.79%; increased coverage also reflects runtime/warmup policies. Oil assessed-row precision97.88%, recall95.73%, but recall including abstentions55.24%,coverage55.08%. Terminal assessed precision97.32%,recall95.25%; recall including abstentions82.06%,coverage83.40%. Fixed tournament7thermal/6oil/6terminal LR configurations selected on validation, then frozen before fresh test.480kill-first checks include hashes, alignment, causality, truth exclusion and missing-data attacks; these are not480independent physical fault experiments. Application checks:80Python+21frontend+5backend=106.209protected model/data files preserved. Sources: ml/final100/reports/FRESH_POST_LOCK_TEST.json; ORIGINAL_TRAINING_README.md; docs/PUBLIC_RELEASE_VALIDATION.md.

## Slide 10
Field validation and the open-source release
The current release is reproducible for local inference. Real asset evidence is the next validation step.
VOLTMIND DISTRIBUTION TRANSFORMER DIGITAL TWIN SYNTHETIC RESEARCH PROTOTYPE
10 / 10
TODAY
Working prototype
Local synthetic replay / upload
Three rating-specific runtimes
Five 100-kVA investigation tools
NEXT
Prove it on real assets
Check real sensor units / cadence
Independent asset commissioning
Test unseen measured histories
THEN
Broaden
Reduce false alerts / abstentions
Investigations for 250 / 630 kVA
Sensor-gateway integration
LATER
Plan ahead
Ageing and remaining-life studies
Fleet-level view across many transformers
Needs long-term field data
MAINTENANCE REVIEW
Inspect persistent deviations and compare matched observations around engineer-entered maintenance.
OPEN-SOURCE PACKAGE
Frontend, backend, Python code, model artifacts, synthetic datasets and tests. MIT terms with retained third-party rights.
ENGINEER OVERSIGHT
Warnings support investigation. Protection, diagnosis and maintenance decisions remain with qualified engineers.
Source: github.com/jereshrirangdotexe/Digital-Twin Next evidence needed: measured SCADA with verified operating context.
Expected benefits remain research goals. Field savings, failure prevention and remaining-life prediction are unvalidated.
Notes: User-provided push logs show public repository main and LFS uploaded. Source URL: https://github.com/jereshrirangdotexe/Digital-Twin. Original project work uses MIT with retained third-party rights. No claim that portable one-command retraining exists: frozen training audit sources depend on historical cached artifacts. Immediate development priorities: measured SCADA, independent calibration, false alarms and abstentions. Current unsupported diagnoses: tank pressure, calibrated vibration/mechanical damage, internal bushing dielectric faults, internal short circuits, measured impedance change, measured hotspot and remaining life. Digital-twin maintenance timing is decision support, not an optimized work order. Sources: README.md; SECURITY.md; THIRD_PARTY_NOTICES.md; ml/final100/ORIGINAL_TRAINING_README.md; docs/FINAL_INTELLIGENCE.md.